## Feeder data
Nepal Electricity Authority
Download Date: 2024-07-25 13:33:26 Consumer Name: Khairini Feeder Consumer Address: Lekhnath SS Consumer No: 000-00-000 MeterNo: 201803002301 Programmed PT ratio: 11000/110 Programmed CT ratio: 300/1 Load Profile (interval 15/30/60 mins): Max XXXXX nos
No. | Date And Time | Power Factor 1 | Power Factor 2 | Power Factor 3 | Average Power factor of a Day
1 | 07-18-2024 09:00:00 | 0.9484 | 0.9631 | 0.9653 | 0.95893
2 | 07-18-2024 09:30:00 | 0.9321 | 0.9342 | 0.9401 | 0.93547
3 | 07-18-2024 10:00:00 | 0.9402 | 0.9426 | 0.9419 | 0.94157
4 | 07-18-2024 10:30:00 | 0.9344 | 0.9409 | 0.9537 | 0.943
5 | 07-18-2024 11:00:00 | 0.9266 | 0.9437 | 0.9429 | 0.93773
6 | 07-18-2024 11:30:00 | 0.9395 | 0.9446 | 0.9551 | 0.9464
7 | 07-18-2024 12:00:00 | 0.936 | 0.9393 | 0.9533 | 0.94287
8 | 07-18-2024 12:30:00 | 0.9107 | 0.9332 | 0.9422 | 0.9287
9 | 07-18-2024 13:00:00 | 0.9437 | 0.9502 | 0.9506 | 0.94817
10 | 07-18-2024 13:30:00 | 0.9562 | 0.9647 | 0.9685 | 0.96313
11 | 07-18-2024 14:00:00 | 0.953 | 0.9586 | 0.9665 | 0.95937
12 | 07-18-2024 14:30:00 | 0.9409 | 0.9566 | 0.9605 | 0.95267
13 | 07-18-2024 15:00:00 | 0.9273 | 0.9288 | 0.9441 | 0.9334
14 | 07-18-2024 15:30:00 | 0.9127 | 0.9243 | 0.9319 | 0.92297
15 | 07-18-2024 16:00:00 | 0.9446 | 0.9481 | 0.959 | 0.95057
16 | 07-18-2024 16:30:00 | 0.8688 | 0.8813 | 0.8705 | 0.87353
17 | 07-18-2024 17:00:00 | 0.8501 | 0.8695 | 0.8583 | 0.8593
18 | 07-18-2024 17:30:00 | 0.8455 | 0.8543 | 0.8456 | 0.84847
19 | 07-18-2024 18:00:00 | 0.8703 | 0.8874 | 0.8581 | 0.87193
20 | 07-18-2024 18:30:00 | 0.8717 | 0.8839 | 0.8611 | 0.87223
21 | 07-18-2024 19:00:00 | 0.9056 | 0.9167 | 0.9027 | 0.90833
22 | 07-18-2024 19:30:00 | 0.9407 | 0.9444 | 0.9415 | 0.9422
23 | 07-18-2024 20:00:00 | 0.9577 | 0.967 | 0.9616 | 0.9621
24 | 07-18-2024 20:30:00 | 0.9407 | 0.9591 | 0.9446 | 0.94813
25 | 07-18-2024 21:00:00 | 0.9483 | 0.9633 | 0.9512 | 0.95427
26 | 07-18-2024 21:30:00 | 0.9202 | 0.9428 | 0.9273 | 0.9301
27 | 07-18-2024 22:00:00 | 0.8735 | 0.8931 | 0.8809 | 0.8825
28 | 07-18-2024 22:30:00 | 0.8672 | 0.8921 | 0.8773 | 0.87887
29 | 07-18-2024 23:00:00 | 0.8642 | 0.8835 | 0.8673 | 0.87167
30 | 07-18-2024 23:30:00 | 0.8893 | 0.9056 | 0.8975 | 0.89747
31 | 07-19-2024 00:00:00 | 0.857 | 0.8712 | 0.8636 | 0.86393
32 | 07-19-2024 00:30:00 | 0.8685 | 0.8876 | 0.8716 | 0.8759
33 | 07-19-2024 01:00:00 | 0.9052 | 0.9177 | 0.9066 | 0.90983
34 | 07-19-2024 01:30:00 | 0.8757 | 0.893 | 0.8915 | 0.88673
35 | 07-19-2024 02:00:00 | 0.8798 | 0.8958 | 0.8707 | 0.8821
36 | 07-19-2024 02:30:00 | 0.8957 | 0.9116 | 0.9028 | 0.90337
37 | 07-19-2024 03:00:00 | 0.865 | 0.8877 | 0.8733 | 0.87533
38 | 07-19-2024 03:30:00 | 0.8904 | 0.9032 | 0.887 | 0.89353
39 | 07-19-2024 04:00:00 | 0.9039 | 0.9165 | 0.9012 | 0.9072
40 | 07-19-2024 04:30:00 | 0.8638 | 0.8755 | 0.8608 | 0.8667
41 | 07-19-2024 05:00:00 | 0.8616 | 0.8791 | 0.8615 | 0.8674
42 | 07-19-2024 05:30:00 | 0.8437 | 0.8707 | 0.8446 | 0.853
43 | 07-19-2024 06:00:00 | 0.8846 | 0.8951 | 0.8699 | 0.8832
44 | 07-19-2024 06:30:00 | 0.8616 | 0.8711 | 0.8572 | 0.8633
45 | 07-19-2024 07:00:00 | 0.8014 | 0.8167 | 0.8111 | 0.80973
46 | 07-19-2024 07:30:00 | 0.8213 | 0.8334 | 0.8351 | 0.82993
47 | 07-19-2024 08:00:00 | 0.8213 | 0.8357 | 0.8342 | 0.8304
48 | 07-19-2024 08:30:00 | 0.829 | 0.8321 | 0.8429 | 0.83467
49 | 07-19-2024 09:00:00 | 0.8257 | 0.8311 | 0.8433 | 0.83337
50 | 07-19-2024 09:30:00 | 0.8092 | 0.8094 | 0.8244 | 0.81433
51 | 07-19-2024 10:00:00 | 0.7911 | 0.7976 | 0.8116 | 0.8001
52 | 07-19-2024 10:30:00 | 0.8418 | 0.8524 | 0.8618 | 0.852
53 | 07-19-2024 11:00:00 | 0.788 | 0.8042 | 0.807 | 0.79973
54 | 07-19-2024 11:30:00 | 0.7921 | 0.8052 | 0.815 | 0.8041
55 | 07-19-2024 12:00:00 | 0.7886 | 0.811 | 0.8236 | 0.80773
56 | 07-19-2024 12:30:00 | 0.8326 | 0.8404 | 0.8417 | 0.83823
57 | 07-19-2024 13:00:00 | 0.7868 | 0.7989 | 0.8146 | 0.8001
58 | 07-19-2024 13:30:00 | 0.7835 | 0.7963 | 0.8117 | 0.79717
59 | 07-19-2024 14:00:00 | 0 | 0 | 0 | 0
60 | 07-19-2024 14:30:00 | 0.7881 | 0.8025 | 0.835 | 0.80853
61 | 07-19-2024 15:00:00 | 0.7717 | 0.7856 | 0.8142 | 0.7905
62 | 07-19-2024 15:30:00 | 0.767 | 0.777 | 0.8145 | 0.78617
63 | 07-19-2024 16:00:00 | 0.7861 | 0.7832 | 0.8121 | 0.7938
64 | 07-19-2024 16:30:00 | 0.781 | 0.7871 | 0.8189 | 0.79567
65 | 07-19-2024 17:00:00 | 0.8113 | 0.8101 | 0.8366 | 0.81933
66 | 07-19-2024 17:30:00 | 0.7798 | 0.7838 | 0.816 | 0.7932
67 | 07-19-2024 18:00:00 | 0.8303 | 0.8401 | 0.8662 | 0.84553
68 | 07-19-2024 18:30:00 | 0.8681 | 0.8674 | 0.8888 | 0.87477
69 | 07-19-2024 19:00:00 | 0.9032 | 0.8925 | 0.9028 | 0.8995
70 | 07-19-2024 19:30:00 | 0.9322 | 0.9137 | 0.9388 | 0.92823
71 | 07-19-2024 20:00:00 | 0.91 | 0.9091 | 0.9407 | 0.91993
72 | 07-19-2024 20:30:00 | 0.9224 | 0.9242 | 0.9419 | 0.9295
73 | 07-19-2024 21:00:00 | 0.9131 | 0.9046 | 0.938 | 0.91857
74 | 07-19-2024 21:30:00 | 0.9047 | 0.9082 | 0.9361 | 0.91633
75 | 07-19-2024 22:00:00 | 0.895 | 0.9077 | 0.9291 | 0.9106
76 | 07-19-2024 22:30:00 | 0.8784 | 0.8839 | 0.9091 | 0.89047
77 | 07-19-2024 23:00:00 | 0.8464 | 0.8654 | 0.8852 | 0.86567
78 | 07-19-2024 23:30:00 | 0.8821 | 0.8894 | 0.9063 | 0.8926
79 | 07-20-2024 00:00:00 | 0.863 | 0.8804 | 0.8944 | 0.87927
80 | 07-20-2024 00:30:00 | 0.8673 | 0.8771 | 0.8945 | 0.87963
81 | 07-20-2024 01:00:00 | 0.8505 | 0.8599 | 0.8809 | 0.86377
82 | 07-20-2024 01:30:00 | 0.8489 | 0.8619 | 0.8803 | 0.8637
83 | 07-20-2024 02:00:00 | 0.8292 | 0.8452 | 0.8743 | 0.84957
84 | 07-20-2024 02:30:00 | 0.9023 | 0.9094 | 0.9281 | 0.91327
85 | 07-20-2024 03:00:00 | 0.8547 | 0.8685 | 0.8929 | 0.87203
86 | 07-20-2024 03:30:00 | 0.8811 | 0.8876 | 0.9037 | 0.8908
87 | 07-20-2024 04:00:00 | 0.8687 | 0.8798 | 0.8967 | 0.88173
88 | 07-20-2024 04:30:00 | 0.8356 | 0.8461 | 0.8643 | 0.84867
89 | 07-20-2024 05:00:00 | 0.8121 | 0.8459 | 0.8611 | 0.8397
90 | 07-20-2024 05:30:00 | 0.9019 | 0.9076 | 0.9362 | 0.91523
91 | 07-20-2024 06:00:00 | 0.8947 | 0.8985 | 0.9435 | 0.91223
92 | 07-20-2024 06:30:00 | 0.8291 | 0.8428 | 0.8493 | 0.8404
93 | 07-20-2024 07:00:00 | 0.776 | 0.7865 | 0.8302 | 0.79757
94 | 07-20-2024 07:30:00 | 0.7238 | 0.7375 | 0.7688 | 0.74337
95 | 07-20-2024 08:00:00 | 0.7812 | 0.7945 | 0.8366 | 0.8041
96 | 07-20-2024 08:30:00 | 0.7247 | 0.7623 | 0.7989 | 0.76197
97 | 07-20-2024 09:00:00 | 0.8382 | 0.8453 | 0.8697 | 0.85107
98 | 07-20-2024 09:30:00 | 0.7696 | 0.7859 | 0.8024 | 0.78597
99 | 07-20-2024 10:00:00 | 0.7555 | 0.7706 | 0.7983 | 0.7748
100 | 07-20-2024 10:30:00 | 0.764 | 0.7812 | 0.8132 | 0.78613
101 | 07-20-2024 11:00:00 | 0.761 | 0.7842 | 0.8053 | 0.7835
102 | 07-20-2024 11:30:00 | 0.882 | 0.8778 | 0.9341 | 0.89797
103 | 07-20-2024 12:00:00 | 0.7621 | 0.7694 | 0.8415 | 0.791
104 | 07-20-2024 12:30:00 | 0.7735 | 0.767 | 0.8505 | 0.797
105 | 07-20-2024 13:00:00 | 0.7009 | 0.7187 | 0.7998 | 0.7398
106 | 07-20-2024 13:30:00 | 0.8576 | 0.8223 | 0.9299 | 0.86993
107 | 07-20-2024 14:00:00 | 0.8499 | 0.8606 | 0.8767 | 0.8624
108 | 07-20-2024 14:30:00 | 0.7809 | 0.7901 | 0.8097 | 0.79357
109 | 07-20-2024 15:00:00 | 0.8267 | 0.8396 | 0.8543 | 0.8402
110 | 07-20-2024 15:30:00 | 0.8544 | 0.8618 | 0.8708 | 0.86233
111 | 07-20-2024 16:00:00 | 0.8166 | 0.8351 | 0.8161 | 0.8226
112 | 07-20-2024 16:30:00 | 0.7874 | 0.8352 | 0.8132 | 0.81193
113 | 07-20-2024 17:00:00 | 0.8272 | 0.8696 | 0.8635 | 0.85343
114 | 07-20-2024 17:30:00 | 0.8055 | 0.837 | 0.8219 | 0.82147
115 | 07-20-2024 18:00:00 | 0.8411 | 0.8986 | 0.8765 | 0.87207
116 | 07-20-2024 18:30:00 | 0.8719 | 0.9135 | 0.9081 | 0.89783
117 | 07-20-2024 19:00:00 | 0.9093 | 0.9277 | 0.9226 | 0.91987
118 | 07-20-2024 19:30:00 | 0.9147 | 0.9484 | 0.9299 | 0.931
119 | 07-20-2024 20:30:00 | 0.9691 | 0.9859 | 0.9859 | 0.9803
120 | 07-20-2024 21:00:00 | 0.8488 | 0.9041 | 0.8819 | 0.87827
121 | 07-20-2024 21:30:00 | 0.8901 | 0.9277 | 0.9137 | 0.9105
122 | 07-20-2024 22:00:00 | 0.86 | 0.9036 | 0.8907 | 0.88477
123 | 07-20-2024 22:30:00 | 0.8525 | 0.9024 | 0.8803 | 0.8784
124 | 07-20-2024 23:00:00 | 0.8747 | 0.9184 | 0.9071 | 0.90007
125 | 07-20-2024 23:30:00 | 0.9022 | 0.9392 | 0.9279 | 0.9231
126 | 07-21-2024 00:00:00 | 0.9131 | 0.9483 | 0.9433 | 0.9349
127 | 07-21-2024 00:30:00 | 0.883 | 0.924 | 0.9104 | 0.9058
128 | 07-21-2024 01:00:00 | 0.8729 | 0.9202 | 0.9077 | 0.90027
129 | 07-21-2024 01:30:00 | 0.8513 | 0.9034 | 0.8763 | 0.877
130 | 07-21-2024 02:00:00 | 0.8605 | 0.9083 | 0.8826 | 0.8838
131 | 07-21-2024 02:30:00 | 0.8288 | 0.8817 | 0.8563 | 0.8556
132 | 07-21-2024 03:00:00 | 0.8485 | 0.9007 | 0.8738 | 0.87433
133 | 07-21-2024 03:30:00 | 0.7949 | 0.854 | 0.8211 | 0.82333
134 | 07-21-2024 04:00:00 | 0.8023 | 0.8588 | 0.8269 | 0.82933
135 | 07-21-2024 04:30:00 | 0.7993 | 0.8472 | 0.8165 | 0.821
136 | 07-21-2024 05:00:00 | 0.8094 | 0.8647 | 0.8388 | 0.83763
137 | 07-21-2024 05:30:00 | 0.8181 | 0.8608 | 0.83 | 0.8363
138 | 07-21-2024 06:00:00 | 0.827 | 0.8671 | 0.8441 | 0.84607
139 | 07-21-2024 06:30:00 | 0.8271 | 0.8571 | 0.8548 | 0.84633
140 | 07-21-2024 07:00:00 | 0.9027 | 0.9584 | 0.6727 | 0.8446
141 | 07-21-2024 07:30:00 | 0.9095 | 0.9569 | 0.9048 | 0.92373
142 | 07-21-2024 08:00:00 | 0.8466 | 0.8763 | 0.8106 | 0.8445
143 | 07-21-2024 08:30:00 | 0.8637 | 0.9163 | 0.8763 | 0.88543
144 | 07-21-2024 09:00:00 | 0.8541 | 0.8928 | 0.8604 | 0.8691
145 | 07-21-2024 09:30:00 | 0.843 | 0.8727 | 0.8497 | 0.85513
146 | 07-21-2024 10:00:00 | 0.8157 | 0.8467 | 0.8226 | 0.82833
147 | 07-21-2024 10:30:00 | 0.8445 | 0.8725 | 0.8444 | 0.8538
148 | 07-21-2024 11:00:00 | 0.8655 | 0.9092 | 0.8582 | 0.87763
149 | 07-21-2024 11:30:00 | 0.82 | 0.8421 | 0.8344 | 0.83217
150 | 07-21-2024 12:00:00 | 0.7796 | 0.7968 | 0.7954 | 0.7906
151 | 07-21-2024 12:30:00 | 0.7323 | 0.8005 | 0.77 | 0.7676
152 | 07-21-2024 13:00:00 | 0.7356 | 0.7604 | 0.7682 | 0.75473
153 | 07-21-2024 13:30:00 | 0.7702 | 0.7933 | 0.7878 | 0.78377
154 | 07-21-2024 14:00:00 | 0.7378 | 0.7626 | 0.7531 | 0.75117
155 | 07-21-2024 14:30:00 | 0.7487 | 0.7775 | 0.771 | 0.76573
156 | 07-21-2024 15:00:00 | 0.7469 | 0.7729 | 0.7684 | 0.76273
157 | 07-21-2024 15:30:00 | 0.7427 | 0.766 | 0.7739 | 0.76087
158 | 07-21-2024 16:00:00 | 0.7707 | 0.7997 | 0.8041 | 0.7915
159 | 07-21-2024 16:30:00 | 0.77 | 0.7818 | 0.7929 | 0.78157
160 | 07-21-2024 17:00:00 | 0.7983 | 0.8084 | 0.8152 | 0.8073
161 | 07-21-2024 17:30:00 | 0.8495 | 0.8625 | 0.872 | 0.86133
162 | 07-21-2024 18:00:00 | 0 | 0 | 0 | 0
163 | 07-21-2024 18:30:00 | 0.9143 | 0.9231 | 0.9126 | 0.91667
164 | 07-21-2024 19:00:00 | 0.8926 | 0.9061 | 0.9097 | 0.9028
165 | 07-21-2024 19:30:00 | 0.9099 | 0.9262 | 0.9124 | 0.91617
166 | 07-21-2024 20:00:00 | 0.9252 | 0.9425 | 0.9359 | 0.93453
167 | 07-21-2024 20:30:00 | 0.9062 | 0.9236 | 0.9198 | 0.91653
168 | 07-21-2024 21:00:00 | 0.9068 | 0.9311 | 0.9156 | 0.91783
169 | 07-21-2024 21:30:00 | 0.8943 | 0.9109 | 0.9045 | 0.90323
170 | 07-21-2024 22:00:00 | 0.9034 | 0.9137 | 0.9 | 0.9057
171 | 07-21-2024 22:30:00 | 0.8915 | 0.9002 | 0.8878 | 0.89317
172 | 07-21-2024 23:00:00 | 0.8912 | 0.9063 | 0.9 | 0.89917
173 | 07-21-2024 23:30:00 | 0.8957 | 0.9089 | 0.9025 | 0.90237
174 | 07-22-2024 00:00:00 | 0.8604 | 0.8735 | 0.8667 | 0.86687
175 | 07-22-2024 00:30:00 | 0.8675 | 0.8813 | 0.8717 | 0.8735
176 | 07-22-2024 01:00:00 | 0.8674 | 0.8812 | 0.8677 | 0.8721
177 | 07-22-2024 01:30:00 | 0.8417 | 0.8615 | 0.846 | 0.84973
178 | 07-22-2024 02:00:00 | 0.8734 | 0.894 | 0.874 | 0.88047
179 | 07-22-2024 02:30:00 | 0.8622 | 0.8842 | 0.859 | 0.86847
180 | 07-22-2024 03:00:00 | 0.8693 | 0.8875 | 0.8699 | 0.87557
181 | 07-22-2024 03:30:00 | 0.8827 | 0.8964 | 0.8876 | 0.8889
182 | 07-22-2024 04:00:00 | 0.8836 | 0.8953 | 0.8762 | 0.88503
183 | 07-22-2024 04:30:00 | 0.8738 | 0.8958 | 0.8792 | 0.88293
184 | 07-22-2024 05:00:00 | 0.8715 | 0.889 | 0.8738 | 0.8781
185 | 07-22-2024 05:30:00 | 0.9182 | 0.9239 | 0.917 | 0.9197
186 | 07-22-2024 06:00:00 | 0.8882 | 0.9025 | 0.8906 | 0.89377
187 | 07-22-2024 06:30:00 | 0.8862 | 0.8888 | 0.8802 | 0.88507
188 | 07-22-2024 07:00:00 | 0.8891 | 0.8842 | 0.8793 | 0.8842
189 | 07-22-2024 07:30:00 | 0.8686 | 0.8698 | 0.8835 | 0.87397
190 | 07-22-2024 08:00:00 | 0.8669 | 0.8732 | 0.8816 | 0.8739
191 | 07-22-2024 08:30:00 | 0.8781 | 0.8796 | 0.8809 | 0.87953
192 | 07-22-2024 09:00:00 | 0.8318 | 0.8442 | 0.8403 | 0.83877
193 | 07-22-2024 09:30:00 | 0.8333 | 0.8341 | 0.8452 | 0.83753
194 | 07-22-2024 10:00:00 | 0.8306 | 0.84 | 0.8456 | 0.83873
195 | 07-22-2024 10:30:00 | 0.814 | 0.8164 | 0.8302 | 0.8202
196 | 07-22-2024 11:00:00 | 0.7747 | 0.7828 | 0.7998 | 0.78577
197 | 07-22-2024 11:30:00 | 0.7774 | 0.7911 | 0.8005 | 0.78967
198 | 07-22-2024 12:00:00 | 0.7844 | 0.7939 | 0.8074 | 0.79523
199 | 07-22-2024 12:30:00 | 0.8316 | 0.8509 | 0.8548 | 0.84577
200 | 07-22-2024 13:00:00 | 0.7908 | 0.8051 | 0.8135 | 0.80313
201 | 07-22-2024 13:30:00 | 0.7879 | 0.8106 | 0.8236 | 0.80737
202 | 07-22-2024 14:00:00 | 0.7821 | 0.7995 | 0.816 | 0.7992
203 | 07-22-2024 14:30:00 | 0.8203 | 0.8325 | 0.8481 | 0.83363
204 | 07-22-2024 15:00:00 | 0.8403 | 0.8492 | 0.868 | 0.8525
205 | 07-22-2024 15:30:00 | 0.8399 | 0.8525 | 0.8615 | 0.8513
206 | 07-22-2024 16:00:00 | 0.7778 | 0.7988 | 0.8041 | 0.79357
207 | 07-22-2024 16:30:00 | 0.7397 | 0.7652 | 0.7655 | 0.7568
208 | 07-22-2024 17:00:00 | 0.7471 | 0.7733 | 0.7753 | 0.76523
209 | 07-22-2024 17:30:00 | 0.8452 | 0.8575 | 0.8682 | 0.85697
210 | 07-22-2024 18:00:00 | 0.8669 | 0.8761 | 0.8715 | 0.8715
211 | 07-22-2024 18:30:00 | 0.868 | 0.8835 | 0.8846 | 0.8787
212 | 07-22-2024 19:00:00 | 0.8986 | 0.8991 | 0.8925 | 0.89673
213 | 07-22-2024 19:30:00 | 0.9336 | 0.9523 | 0.9433 | 0.94307
214 | 07-22-2024 20:00:00 | 0.9217 | 0.9456 | 0.9387 | 0.93533
215 | 07-22-2024 20:30:00 | 0.9127 | 0.9392 | 0.9382 | 0.93003
216 | 07-22-2024 21:00:00 | 0.9117 | 0.938 | 0.934 | 0.9279
217 | 07-22-2024 21:30:00 | 0.917 | 0.9412 | 0.9428 | 0.93367
218 | 07-22-2024 22:00:00 | 0.9049 | 0.9357 | 0.9423 | 0.92763
219 | 07-22-2024 22:30:00 | 0.9186 | 0.9376 | 0.9391 | 0.93177
220 | 07-22-2024 23:00:00 | 0.89 | 0.913 | 0.9127 | 0.90523
221 | 07-22-2024 23:30:00 | 0.9176 | 0.9322 | 0.93 | 0.9266
222 | 07-23-2024 00:00:00 | 0.8801 | 0.8984 | 0.8977 | 0.89207
223 | 07-23-2024 00:30:00 | 0.8961 | 0.9149 | 0.9137 | 0.90823
224 | 07-23-2024 01:00:00 | 0.9044 | 0.9203 | 0.9231 | 0.91593
225 | 07-23-2024 01:30:00 | 0.8831 | 0.9043 | 0.903 | 0.8968
226 | 07-23-2024 02:00:00 | 0.8737 | 0.8956 | 0.8961 | 0.88847
227 | 07-23-2024 02:30:00 | 0.8454 | 0.876 | 0.8712 | 0.8642
228 | 07-23-2024 03:00:00 | 0.8541 | 0.8804 | 0.8757 | 0.87007
229 | 07-23-2024 03:30:00 | 0.8732 | 0.907 | 0.9222 | 0.9008
230 | 07-23-2024 04:00:00 | 0.8608 | 0.8901 | 0.882 | 0.87763
231 | 07-23-2024 04:30:00 | 0.8596 | 0.8827 | 0.8752 | 0.8725
232 | 07-23-2024 05:00:00 | 0.8757 | 0.8975 | 0.8849 | 0.88603
233 | 07-23-2024 05:30:00 | 0.8946 | 0.9062 | 0.9043 | 0.9017
234 | 07-23-2024 06:00:00 | 0.899 | 0.92 | 0.9095 | 0.9095
235 | 07-23-2024 06:30:00 | 0.8794 | 0.8925 | 0.9068 | 0.8929
236 | 07-23-2024 07:00:00 | 0.8629 | 0.8708 | 0.8766 | 0.8701
237 | 07-23-2024 07:30:00 | 0.8642 | 0.8689 | 0.8672 | 0.86677
238 | 07-23-2024 08:00:00 | 0.8715 | 0.8873 | 0.9058 | 0.8882
239 | 07-23-2024 08:30:00 | 0.8559 | 0.8673 | 0.8723 | 0.86517
240 | 07-23-2024 09:00:00 | 0.8623 | 0.8893 | 0.8729 | 0.87483
241 | 07-23-2024 09:30:00 | 0.8475 | 0.8709 | 0.8707 | 0.86303
242 | 07-23-2024 10:00:00 | 0.821 | 0.8365 | 0.8487 | 0.8354
243 | 07-23-2024 10:30:00 | 0.818 | 0.8353 | 0.842 | 0.83177
244 | 07-23-2024 11:00:00 | 0.7845 | 0.8104 | 0.816 | 0.80363
245 | 07-23-2024 11:30:00 | 0.8288 | 0.8451 | 0.8526 | 0.84217
246 | 07-23-2024 12:00:00 | 0.752 | 0.7802 | 0.7696 | 0.76727
247 | 07-23-2024 12:30:00 | 0.7365 | 0.767 | 0.7641 | 0.75587
248 | 07-23-2024 13:00:00 | 0.7649 | 0.7851 | 0.7801 | 0.7767
249 | 07-23-2024 13:30:00 | 0.7499 | 0.7677 | 0.7529 | 0.75683
250 | 07-23-2024 14:00:00 | 0.7791 | 0.8087 | 0.8006 | 0.79613
251 | 07-23-2024 14:30:00 | 0.7713 | 0.7844 | 0.7849 | 0.7802
252 | 07-23-2024 15:00:00 | 0.7745 | 0.7948 | 0.794 | 0.78777
253 | 07-23-2024 15:30:00 | 0.7595 | 0.7724 | 0.768 | 0.76663
254 | 07-23-2024 16:00:00 | 0.7798 | 0.8056 | 0.7901 | 0.79183
255 | 07-23-2024 16:30:00 | 0.846 | 0.865 | 0.8592 | 0.85673
256 | 07-23-2024 17:00:00 | 0.8513 | 0.86 | 0.8636 | 0.8583
257 | 07-23-2024 17:30:00 | 0.8667 | 0.8741 | 0.8858 | 0.87553
258 | 07-23-2024 18:00:00 | 0.8736 | 0.8886 | 0.889 | 0.88373
259 | 07-23-2024 18:30:00 | 0.8667 | 0.9017 | 0.8752 | 0.8812
260 | 07-23-2024 19:00:00 | 0.8847 | 0.8888 | 0.889 | 0.8875
261 | 07-23-2024 19:30:00 | 0.9436 | 0.9402 | 0.9395 | 0.9411
262 | 07-23-2024 20:00:00 | 0.9277 | 0.9426 | 0.9454 | 0.93857
263 | 07-23-2024 20:30:00 | 0.9185 | 0.9326 | 0.9365 | 0.9292
264 | 07-23-2024 21:00:00 | 0.9353 | 0.9461 | 0.9476 | 0.943
265 | 07-23-2024 21:30:00 | 0.9329 | 0.9475 | 0.9501 | 0.9435
266 | 07-23-2024 22:00:00 | 0.8997 | 0.9201 | 0.9162 | 0.912
267 | 07-23-2024 22:30:00 | 0.8881 | 0.9096 | 0.9021 | 0.89993
268 | 07-23-2024 23:00:00 | 0.8894 | 0.9125 | 0.9095 | 0.9038
269 | 07-23-2024 23:30:00 | 0.8919 | 0.9121 | 0.914 | 0.906
270 | 07-24-2024 00:00:00 | 0.8984 | 0.913 | 0.9146 | 0.90867
271 | 07-24-2024 00:30:00 | 0.8839 | 0.9046 | 0.9069 | 0.89847
272 | 07-24-2024 01:00:00 | 0.8877 | 0.9074 | 0.9039 | 0.89967
273 | 07-24-2024 01:30:00 | 0.8834 | 0.9004 | 0.9016 | 0.89513
274 | 07-24-2024 02:00:00 | 0.8866 | 0.9074 | 0.9045 | 0.8995
275 | 07-24-2024 02:30:00 | 0.8561 | 0.8775 | 0.8751 | 0.86957
276 | 07-24-2024 03:00:00 | 0.8576 | 0.8865 | 0.8752 | 0.8731
277 | 07-24-2024 03:30:00 | 0.8726 | 0.8968 | 0.8911 | 0.88683
278 | 07-24-2024 04:00:00 | 0.834 | 0.8644 | 0.8536 | 0.85067
279 | 07-24-2024 04:30:00 | 0.8941 | 0.9165 | 0.9019 | 0.90417
280 | 07-24-2024 05:00:00 | 0.9289 | 0.9534 | 0.9698 | 0.9507
281 | 07-24-2024 06:00:00 | 0.883 | 0.8828 | 0.8856 | 0.8838
282 | 07-24-2024 06:30:00 | 0.9328 | 0.9432 | 0.9339 | 0.93663
283 | 07-24-2024 07:00:00 | 0.8438 | 0.8533 | 0.8608 | 0.85263
284 | 07-24-2024 07:30:00 | 0.841 | 0.844 | 0.8595 | 0.84817
285 | 07-24-2024 08:00:00 | 0.8574 | 0.8672 | 0.8791 | 0.8679
286 | 07-24-2024 08:30:00 | 0.8185 | 0.8393 | 0.8448 | 0.8342
287 | 07-24-2024 09:00:00 | 0.8147 | 0.829 | 0.8368 | 0.82683
288 | 07-24-2024 09:30:00 | 0.8107 | 0.8144 | 0.8317 | 0.81893
289 | 07-24-2024 10:00:00 | 0.781 | 0.803 | 0.8045 | 0.79617
290 | 07-24-2024 10:30:00 | 0.7854 | 0.8061 | 0.8153 | 0.80227
291 | 07-24-2024 11:00:00 | 0.792 | 0.8127 | 0.8212 | 0.80863
292 | 07-24-2024 11:30:00 | 0.7911 | 0.8148 | 0.8142 | 0.8067
293 | 07-24-2024 12:00:00 | 0.7895 | 0.8247 | 0.8187 | 0.81097
294 | 07-24-2024 12:30:00 | 0.7671 | 0.7964 | 0.798 | 0.78717
295 | 07-24-2024 13:00:00 | 0.8213 | 0.8329 | 0.8446 | 0.83293
296 | 07-24-2024 13:30:00 | 0.8087 | 0.8323 | 0.8292 | 0.8234
297 | 07-24-2024 14:00:00 | 0.796 | 0.815 | 0.8135 | 0.80817
298 | 07-24-2024 14:30:00 | 0.7231 | 0.7373 | 0.741 | 0.7338
299 | 07-24-2024 15:00:00 | 0.7384 | 0.7612 | 0.7686 | 0.75607
300 | 07-24-2024 15:30:00 | 0.8354 | 0.8527 | 0.8586 | 0.8489
301 | 07-24-2024 16:00:00 | 0.8097 | 0.827 | 0.8335 | 0.8234
302 | 07-24-2024 16:30:00 | 0.8389 | 0.8644 | 0.8638 | 0.8557
303 | 07-24-2024 17:00:00 | 0.8365 | 0.8671 | 0.8531 | 0.85223
304 | 07-24-2024 17:30:00 | 0.8679 | 0.8808 | 0.8724 | 0.8737
305 | 07-24-2024 18:00:00 | 0.8669 | 0.8974 | 0.8915 | 0.88527
306 | 07-24-2024 18:30:00 | 0.861 | 0.8864 | 0.8914 | 0.8796
|  |  | Average pf of a Feeder |  | 0.85797

## LIne load data
[17 empty] | Lf | 0.8
[17 empty] | PF | 0.85797
[16 empty] | Transformer Location | With Load Factor(kVA) |  | Transformer Capacity (kVA)
Bus ID | Branch Number | From Bus | To Bus | Length (km) | Type of Conductor(mm2) | R(ohm) | X(ohm) | PL (KW) | QL(KVAR) | R |  | X
Substation |  |  | 1 |  |  |  |  | 0 | 0 | [7 empty] | 0 |  | 0
Hotel Ravi Mahal | 1 | 1 | 2 | 0.75 | Dog | 0.20588 | 0.23625 | 103.2 | 61.2 |  | 850 |  |  |  |  | Hotel Ravi Mahal | 120 |  | 150
DadaNaak | 2 | 2 | 3 | 0.15 | Dog | 0.041175 | 0.04725 | 137.6 | 81.6 |  | 250 |  |  |  |  | DadaNaak | 160 |  | 200
NTC Office | 3 | 3 | 4 | 0.4 | Dog | 0.1098 | 0.126 | 17.2 | 10.2 |  | 500 |  |  |  |  | NTC Office | 20 |  | 25
Sujal Foods | 4 | 4 | 5 | 0.35 | Dog | 0.096075 | 0.11025 | 433.44 | 257.04 |  | 450 |  |  | R | X | Sujal Foods | 504 |  | 630
Bhatyako Chawki | 5 | 5 | 6 | 3 | Dog | 0.8235 | 0.945 | 34.4 | 20.4 |  | 3100 |  | Dog | 0.2745 | 0.315 | Bhatyako Chawki | 40 |  | 50
Grihyalaxmi | 6 | 6 | 7 | 0.1 | Dog | 0.02745 | 0.0315 | 137.6 | 81.6 |  | 200 |  | Rabbit | 0.5449 | 0.335 | Grihyalaxmi | 160 |  | 200
Tallo Gagangauda | 7 | 7 | 8 | 0.2 | Dog | 0.0549 | 0.063 | 137.6 | 81.6 |  | 300 |  | Weasel | 0.9116 | 0.345 | Tallo Gagangauda | 160 |  | 200
Buddiman | 8 | 8 | 9 | 1.8 | Dog | 0.4941 | 0.567 | 137.6 | 81.6 |  | 1900 |  |  |  |  | Buddiman | 160 |  | 200
Lameyhaat | 9 | 9 | 10 | 0.09 | Dog | 0.024705 | 0.02835 | 68.8 | 40.8 |  | 200 |  |  |  |  | Lameyhaat | 80 |  | 100
Majuwa | 10 | 10 | 11 | 0.6 | Dog | 0.1647 | 0.189 | 137.6 | 81.6 |  | 700 |  |  |  |  | Majuwa | 160 |  | 200
Kotre | 11 | 11 | 12 | 1.4 | Dog | 0.3843 | 0.441 | 137.6 | 81.6 |  | 1500 |  |  |  |  | Kotre | 160 |  | 200
Kotre Pole Plant | 12 | 12 | 13 | 1.1 | Dog | 0.30195 | 0.3465 | 137.6 | 81.6 |  | 1200 |  |  |  |  | Kotre Pole Plant | 160 |  | 200
Hotel Ravi Mahal | 13 | 13 | 14 | 0.4 | Rabbit | 0.21796 | 0.134 | 137.6 | 81.6 |  | 500 |  |  |  |  | Hotel Ravi Mahal | 160 |  | 200
Sujal Foods | 14 | 2 | 15 | 0.1 | Rabbit | 0.05449 | 0.0335 | 103.2 | 61.2 |  | 100 |  |  |  |  | Sujal Foods | 120 |  | 150
Bhandari Rice Mill | 15 | 5 | 16 | 1.2 | Rabbit | 0.65388 | 0.402 | 68.8 | 40.8 |  | 1300 |  |  |  |  | Bhandari Rice Mill | 80 |  | 100
Tallo Gagangauda | 16 | 16 | 17 | 0.1 | Rabbit | 0.05449 | 0.0335 | 68.8 | 40.8 |  | 200 |  |  |  |  | Tallo Gagangauda | 80 |  | 100
Chhaplayang | 17 | 8 | 18 | 0.9 | Rabbit | 0.49041 | 0.3015 | 68.8 | 40.8 |  | 1000 |  |  |  |  | Chhaplayang | 80 |  | 100
Thulo Pudi | 18 | 18 | 19 | 0.6 | Rabbit | 0.32694 | 0.201 | 34.4 | 20.4 |  | 700 |  |  |  |  | Thulo Pudi | 40 |  | 50
Ncell | 19 | 19 | 20 | 1.8 | Rabbit | 0.98082 | 0.603 | 17.2 | 10.2 |  | 1900 |  |  |  |  | Ncell | 20 |  | 25
Majuwa | 20 | 20 | 21 | 0.1 | Rabbit | 0.05449 | 0.0335 | 34.4 | 20.4 |  | 100 |  |  |  |  | Majuwa | 40 |  | 50
Bio Gas | 21 | 11 | 22 | 0.9 | Weasel | 0.82044 | 0.3105 | 68.8 | 40.8 |  | 1000 |  |  |  |  | Bio Gas | 80 |  | 100
Bio Gas | 22 | 22 | 23 | 0.1 | Weasel | 0.09116 | 0.0345 | 34.4 | 20.4 |  | 100 |  |  |  |  | Bio Gas | 40 |  | 50
Eakleya Faat I | 23 | 22 | 24 | 0.9 | Weasel | 0.82044 | 0.3105 | 68.8 | 40.8 |  | 1000 |  |  |  |  | Eakleya Faat I | 80 |  | 100
Kotre | 24 | 24 | 25 | 0.6 | Rabbit | 0.32694 | 0.201 | 68.8 | 40.8 |  | 700 |  |  |  |  | Kotre | 80 |  | 100
Tallo Pudi | 25 | 12 | 26 | 2 | Rabbit | 1.0898 | 0.67 | 68.8 | 40.8 |  | 2100 |  |  |  |  | Tallo Pudi | 80 |  | 100
Tallo Pudi | 26 | 26 | 27 | 0.1 | Rabbit | 0.05449 | 0.0335 | 17.2 | 10.2 |  | 150 |  |  |  |  | Tallo Pudi | 20 |  | 25
Uppalo Pudi I | 27 | 26 | 28 | 1.4 | Rabbit | 0.76286 | 0.469 | 34.4 | 20.4 |  | 1500 |  |  |  |  | Uppalo Pudi I | 40 |  | 50
Uppalo Pudi II | 28 | 28 | 29 | 0.6 | Rabbit | 0.32694 | 0.201 | 34.4 | 20.4 |  | 700 |  |  |  |  | Uppalo Pudi II | 40 |  | 50
[8 empty] | 2549.04 | 1511.64 |  | 24200 | [5 empty] | 2964 |  | 3705

## Location
Branch Number | From Bus | To Bus | From | To
1 | 1 | 2 | Substation | Hotel Ravi mahal(Aarghau Chowk)
2 | 2 | 3 | Hotel Ravi Mahal | DadaNaak
3 | 3 | 4 | DadaNaak | NTC Office
4 | 4 | 5 | NTC Office | Sujal Foods
5 | 5 | 6 | Sujal Foods | Bhatyako Chawki
6 | 6 | 7 | Bhatyako Chawki | Grihyalaxmi
7 | 7 | 8 | Grihyalaxmi | Tallo Gagangauda
8 | 8 | 9 | Tallo Gagangauda | Buddiman
9 | 9 | 10 | Buddiman | Lameyhaat
10 | 10 | 11 | Lameyhaat | Majuwa
11 | 11 | 12 | Majuwa | Kotre
12 | 12 | 13 | Kotre | Kotre Pole Plant
13 | 13 | 14 | Kotre Pole Plant | Yaso Santi
14 | 2 | 15 | Hotel Ravi Mahal | GachhyaFaat
15 | 5 | 16 | Sujal Foods | Bhandari Rice Mill
16 | 16 | 17 | Bhandari Rice Mill | BhandariDhik
17 | 8 | 18 | Tallo Gagangauda | Chhaplayang
18 | 18 | 19 | Chhaplayang | Thulo Pudi
19 | 19 | 20 | Thulo Pudi | Ncell
20 | 20 | 21 | Ncell | Aapukaseri
21 | 11 | 22 | Majuwa | Bio Gas
22 | 22 | 23 | Bio Gas | Block Factory
23 | 22 | 24 | Bio Gas | Eakleya Faat I
24 | 24 | 25 | Eakleya Faat I | Eakleya Faat II
25 | 12 | 26 | Kotre | Tallo Pudi
26 | 26 | 27 | Tallo Pudi | Ncell
27 | 26 | 28 | Tallo Pudi | Uppalo Pudi I
28 | 28 | 29 | Uppalo Pudi I | Uppalo Pudi II

## 33 test Bus Line Data
Bus No | From | To | R (ohm) | X (ohm)
1 | 1 | 2 | 0.0922 | 0.047
2 | 2 | 3 | 0.493 | 0.2511
3 | 3 | 4 | 0.366 | 0.1864
4 | 4 | 5 | 0.3811 | 0.1941
4 | 5 | 6 | 0.819 | 0.707
6 | 6 | 7 | 0.1872 | 0.6188
7 | 7 | 8 | 0.7114 | 0.2351
8 | 8 | 9 | 1.03 | 0.74
9 | 9 | 10 | 1.044 | 0.74
10 | 10 | 11 | 0.1966 | 0.065
11 | 11 | 12 | 0.3744 | 0.1238
12 | 12 | 13 | 1.468 | 1.155
13 | 13 | 14 | 0.5416 | 0.7129
14 | 14 | 15 | 0.591 | 0.526
15 | 15 | 16 | 0.7463 | 0.545
16 | 16 | 17 | 1.289 | 1.721
17 | 17 | 18 | 0.732 | 0.574
18 | 2 | 19 | 0.264 | 0.2565
19 | 19 | 20 | 1.5042 | 1.3554
20 | 20 | 21 | 0.4095 | 0.4784
21 | 21 | 22 | 0.7089 | 0.9373
22 | 3 | 23 | 0.4512 | 0.3083
23 | 23 | 24 | 0.898 | 0.7091
24 | 24 | 25 | 0.896 | 0.7011
25 | 6 | 26 | 0.203 | 0.1034
26 | 26 | 27 | 0.2842 | 0.1447
27 | 27 | 28 | 1.059 | 0.9337
28 | 28 | 29 | 0.8042 | 0.7006
29 | 29 | 30 | 0.5075 | 0.2585
30 | 30 | 31 | 0.9744 | 0.963
31 | 31 | 32 | 0.3105 | 0.3619
32 | 32 | 33 | 0.341 | 0.5302

## 33 test Bus Loaad Data
Bus No | P (KW) | Q (KVAR)
1 | 0 | 0
2 | 100 | 60
3 | 90 | 40
4 | 120 | 80
4 | 60 | 30
6 | 60 | 20
7 | 200 | 100
8 | 200 | 100
9 | 60 | 20
10 | 60 | 20
11 | 45 | 30
12 | 60 | 35
13 | 60 | 35
14 | 120 | 80
15 | 60 | 10
16 | 60 | 20
17 | 60 | 20
18 | 90 | 40
19 | 90 | 40
20 | 90 | 40
21 | 90 | 40
22 | 90 | 40
23 | 90 | 50
24 | 420 | 200
25 | 420 | 200
26 | 60 | 25
27 | 60 | 25
28 | 60 | 20
29 | 120 | 70
30 | 200 | 600
31 | 150 | 70
32 | 210 | 100
33 | 60 | 40

## Voltage Power Loss33 Bus
Bus No | Voltage (pu) | Branch No | Active Power Loss(KW) | Active Power Loss(KVAR)
1 | 1 |  | 0 | 0
2 | 0.99704 | 1-2 | 12.1933 | 15.3605
3 | 0.98298 | 2-3 | 51.5711 | 48.2925
4 | 0.97552 | 3-4 | 19.7934 | 21.6544
5 | 0.96815 | 4-5 | 18.5931 | 21.0362
6 | 0.9498 | 5-6 | 38.0257 | 74.063
7 | 0.94634 | 6-7 | 1.9131 | 52.056
8 | 0.9415 | 7-8 | 4.8342 | 17.2425
9 | 0.93524 | 8-9 | 4.1773 | 38.604
10 | 0.92944 | 9-10 | 3.5575 | 36.7223
11 | 0.92858 | 10-11 | 0.55307 | 3.0606
12 | 0.92708 | 11-12 | 0.88022 | 1.3372
13 | 0.92099 | 12-13 | 2.6638 | 3.3889
14 | 0.91875 | 13-14 | 0.72856 | 1.622
15 | 0.91734 | 14-15 | 0.35686 | 0.62321
16 | 0.91598 | 15-16 | 0.28132 | 0.45256
17 | 0.91398 | 16-17 | 0.25148 | 0.89989
18 | 0.91337 | 17-18 | 0.053103 | 0.17238
19 | 0.99618 | 2-19 | 0.25926 | 3.9404
20 | 0.99261 | 19-20 | 0.83271 | 18.2702
21 | 0.99191 | 20-21 | 0.10082 | 5.5922
22 | 0.99127 | 21-22 | 0.043662 | 9.1812
23 | 0.97939 | 3-23 | 3.1812 | 2.4831
24 | 0.97272 | 23-24 | 5.1432 | 4.6992
25 | 0.9694 | 24-25 | 1.2873 | 1.3175
26 | 0.94788 | 6-26 | 2.594 | 0.082607
27 | 0.94533 | 26-27 | 3.3211 | 0.074781
28 | 0.93393 | 27-28 | 11.2766 | 0.27629
29 | 0.92574 | 28-29 | 7.818 | 0.098858
30 | 0.92222 | 29-30 | 3.8881 | 1.9889
31 | 0.91804 | 30-31 | 1.5928 | 1.581
32 | 0.91712 | 31-32 | 0.21308 | 0.24943
33 | 0.91683 | 32-33 | 0.013162 | 0.020552

## Voltage Power Loss Khaireni
Bus No | Voltage (pu) | Branch No | Active Power Loss(KW) | Reactive Power Loss(KVAR)
1 | 1 |  | 0 | 0
2 | 0.99145 | 1-2 | 18.3515 | 21.0591
3 | 0.98913 | 2-3 | 4.5838 | 5.2601
4 | 0.98477 | 3-4 | 8.1543 | 9.3573
5 | 0.98087 | 4-5 | 7.2281 | 8.2945
6 | 0.96091 | 5-6 | 27.6791 | 31.763
7 | 0.95965 | 6-7 | 1.7116 | 1.9641
8 | 0.95792 | 7-8 | 2.1456 | 2.4622
9 | 0.94919 | 8-9 | 8.6964 | 9.9794
10 | 0.94838 | 9-10 | 0.71106 | 0.81597
11 | 0.94574 | 10-11 | 2.1647 | 2.484
12 | 0.94234 | 11-12 | 1.6738 | 1.9207
13 | 0.94102 | 12-13 | 0.31486 | 0.36131
14 | 0.94057 | 13-14 | 0.065137 | 0.040045
15 | 0.99138 | 2-15 | 0.006596 | 0.0040552
16 | 0.97975 | 5-16 | 0.1561 | 0.095967
17 | 0.97966 | 16-17 | 0.0060043 | 0.0036914
18 | 0.95693 | 8-18 | 0.15943 | 0.098018
19 | 0.95654 | 18-19 | 0.03447 | 0.021192
20 | 0.95591 | 19-20 | 0.0337 | 0.020719
21 | 0.95589 | 20-21 | 0.00078832 | 0.00048465
22 | 0.94337 | 11-22 | 0.66473 | 0.25157
23 | 0.94333 | 22-23 | 0.0013542 | 0.0005125
24 | 0.94201 | 22-24 | 0.21735 | 0.082258
25 | 0.9417 | 24-25 | 0.022743 | 0.013983
26 | 0.94022 | 12-26 | 0.34675 | 0.21318
27 | 0.9402 | 26-27 | 0.00030557 | 0.00018786
28 | 0.93954 | 26-28 | 0.048968 | 0.030105
29 | 0.93939 | 28-29 | 0.0057139 | 0.0035128
|  |  | 85.1849 | 96.6013